## Sheet1
2023 Test Result for the City of Drayton
Contaminant | MCLG | MCL | Level Detected | Units | Range | Date (year) | Violation Yes/No Other Info | Likely Source of Contamination
Lead/Copper
Lead | 0 | AL=15ppb | 3.74 | ppb | N/A | 2022-08-31 | 0 Sites exceeded AL | Plumbing corrosion
Copper | 0 | AL=1.3ppm | 0.385 | ppm | N/A | 2022-08-31 | 0 Sites exceeded AL | Plumbing corrosion
Microbiological Contaminants
Turbidity | N/A | TT=.3 | 0.074 | NTU | N/A | 2023 | 100% of samples met Turbidity Limits | Soil runoff
Inorganic Contaminants
Arsenic | N/A | 10 | 1.7 | ppb | N/A | 2016-03-16 | No | Erosion natural deposits
Barium | 2 | 2 | 0.0323 | ppm | N/A | 2017-04-12 | No | Erosion natural deposits
Fluoride | 4 | 4 | 0.674 | ppm | N/A | 2017-05-16 | No | Erosion natural deposits
Nitrate-Nitrite | 10 | 10 | 0.379 | ppm | N/A | 2023-04-25 | No | Erosion natural deposits
Selenium | 50 | 50 | 1.29 | ppb | N/A | 2017-04-12 | No | Erosion natural deposits
Radioactive Contaminants
GROSS ALPHA, INCLDNG RA, EXCLDNG RN & U | 15 | 15 | ND | pCi/l | N/A | 2017-06-20 | No | Erosion natural deposits
Radium, Combined (226,228) | 0 | 5 | 0.37 | pCi/l | N/A | 2017-06-20 | No | Erosion natural deposits
Uranium, Combined | 0 | 30 | 0.88 | ppb | N/A | 2017-06-20 | No | Erosion natural deposits
Stage 2 Disinfection Byproducts (TTHM/HAA5)
HAA5 | 0 | 60 | 19 | ppb | 5.69 to 17.45 | 2023-03-31 | No | By-product of drinking water chlorination
TTHM | 0 | 80 | 43 | ppb | 16.21 to 63.86 | 2023-09-30 | No | By-product of drinking water chlorination
Disinfectants
Chloramine | MRDL=4.0 | MRDL=4.0 | 1.9 | ppm | 1.82 to 1.88 | 2023-03-31 | No | Water additive to control microbes
Unregulated Contaminants
Alkalinity, Carbonate | 0 | 0 | 4 | ppm | ND to 4 | 2023-12-13 | No
Calcium | 0 | 0 | 41.3 | ppm | n/a | 2017-04-12 | No
Bicarbonate AS HCO3 | 0 | 0 | 454 | ppm | 152-454 | 2023-12-13 | No
Chlororide | 0 | 0 | 36.1 | ppm | n/a | 2017-04-12 | No
Conductivity @25 C UMHOS/CM | 0 | 0 | 595 | umho/cm | n/a | 2017-04-12 | No
Hardness, Total (As CACO3) | 0 | 0 | 203 | ppm | n/a | 2017-04-12 | No
Magnesium | 0 | 0 | 24.3 | ppm | n/a | 2017-04-12 | No
Nickel | 0 | 0 | 0.00214 | ppm | n/a | 2017-04-12 | No
PH | 0 | 0 | 7.58 | ppm | PH | 2017-04-12 | No
Potassium | 0 | 0 | 4.3 | ppm | n/a | 2017-04-12 | No
Sodium | 0 | 0 | 30.2 | ppm | n/a | 2017-04-12 | No
Sodium Adsorption Ratio | 0 | 0 | 0.92 | obsvns | n/a | 2017-04-12 | No
Sulfate | 0 | 0 | 154 | ppm | 149-154 | 2017-04-12 | No
TDS | 0 | 0 | 340 | ppm | n/a | 2017-04-12 | No
Zinc | 0 | 0 | 0.00115 | ppm | n/a | 2017-04-12 | No
Total Organic Carbon Removal
Alkalinity-Source | 0 | 0 | 372 | MG/L | 125.00 to 372.00 | 2023-11-30 | No | Naturally present in environment
Carbon, Total Organic (TOC)- Finished | 0 | 0 | 2.92 | MG/L | 0.83 to 2.92 | 2023-01-31 | No | Naturally present in environment
Carbon, Total Organic (TOC)- Source | 0 | 0 | 126 | MG/L | 11.10 to 126.00 | 2023-11-30 | No | Naturally present in environment
Synthetic Organic Contaminants including Pesticides and Herbicides
Pentachlorophenol | 0 | 1 | 0.03 | ppb | N/A | 2017-05-23 | No | Discharge from wood preserving factories